## 风机基础数据
设防烈度 | 承载力 | 基础型式 | 极限荷载 | 底板半径R | 棱台顶面半径R1 | 台柱半径R2 | 底板外缘高度H1 | 底板棱台高度H2 | 台柱高度H3 | 桩直径 | 根数 | 长度 | 单台总桩长 | 面积m2 | 体积m3 | 垫层 | M48预应力 锚栓（m) | C80二次灌浆 | 土方开挖 | 石方开挖 | 土石方回填
Fortificationintensity | Bearingcapacity | Basictype | Ultimateload | FloorradiusR | R1 | R2 | H1 | H2 | H3 | Pilediameter | number | length | Singlepilelength | Area | Volume | Cushion | M48PrestressedAnchor | C80secondarygrouting | Earth excavation | Stone excavation | Earthwork backfill
6 | 180 | 扩展基础 | 50000 | 9.5 | 3 | 3 | 1 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 283.5287 | 466.6836 | 43.4294 | 480 | 2 | 923.4171 | 230.8543 | 644.1584
6 | 180 | 扩展基础 | 60000 | 10 | 3 | 3 | 1 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 314.1593 | 540.5634 | 48.0711 | 504 | 2 | 1075.0819 | 268.7705 | 755.2179
6 | 180 | 扩展基础 | 70000 | 10.25 | 3 | 3 | 1 | 1.6 | 1 | 0 | 0 | 0 | 0 | 330.0636 | 600.9736 | 50.4803 | 552 | 2 | 1257.2889 | 314.3222 | 920.1573
6 | 180 | 扩展基础 | 80000 | 10.25 | 3 | 3 | 1 | 1.7 | 1 | 0 | 0 | 0 | 0 | 330.0636 | 616.1383 | 50.4803 | 564 | 2 | 1290.8166 | 322.7042 | 946.9022
6 | 180 | 扩展基础 | 90000 | 10.75 | 3 | 3 | 1 | 1.7 | 1 | 0 | 0 | 0 | 0 | 363.0503 | 670.4879 | 55.4754 | 564 | 2 | 1404.9947 | 351.2487 | 1030.2801
6 | 180 | 扩展基础 | 100000 | 11 | 3 | 3 | 1 | 1.8 | 1 | 0 | 0 | 0 | 0 | 380.1327 | 715.6548 | 58.0613 | 576 | 2 | 1501.9213 | 375.4803 | 1103.6855
6 | 180 | 扩展基础 | 110000 | 11.5 | 3 | 3 | 1.1 | 1.8 | 1 | 0 | 0 | 0 | 0 | 415.4756 | 816.5785 | 63.4099 | 588 | 2 | 1667.6881 | 416.922 | 1204.6217
6 | 180 | 扩展基础 | 120000 | 12 | 3 | 3 | 1.2 | 1.8 | 1 | 0 | 0 | 0 | 0 | 452.3893 | 927.3982 | 68.9941 | 600 | 2 | 1844.9782 | 461.2445 | 1309.8305
6 | 180 | 预制桩承台基础 | 50000 | 9 | 3 | 3 | 1 | 1.2 | 0.8 | 0.6 | 20 | 20 | 400 | 254.469 | 424.115 | 39.0233 | 480 | 2 | 839.8947 | 209.9737 | 586.7301
6 | 180 | 预制桩承台基础 | 60000 | 9.5 | 3 | 3 | 1 | 1.2 | 0.8 | 0.6 | 22 | 20 | 440 | 283.5287 | 466.6836 | 43.4294 | 480 | 2 | 923.4171 | 230.8543 | 644.1584
6 | 180 | 预制桩承台基础 | 70000 | 9.5 | 3 | 3 | 1 | 1.2 | 0.8 | 0.6 | 24 | 20 | 480 | 283.5287 | 466.6836 | 43.4294 | 480 | 2 | 923.4171 | 230.8543 | 644.1584
6 | 180 | 预制桩承台基础 | 80000 | 10 | 3 | 3 | 1 | 1.4 | 1 | 0.6 | 26 | 20 | 520 | 314.1593 | 546.2182 | 48.0711 | 528 | 2 | 1139.2659 | 284.8165 | 829.7931
6 | 180 | 预制桩承台基础 | 90000 | 10 | 3 | 3 | 1 | 1.4 | 1 | 0.6 | 28 | 20 | 560 | 314.1593 | 546.2182 | 48.0711 | 528 | 2 | 1139.2659 | 284.8165 | 829.7931
6 | 180 | 预制桩承台基础 | 100000 | 10.25 | 3 | 3 | 1.1 | 1.4 | 1 | 0.6 | 30 | 20 | 600 | 330.0636 | 603.6505 | 50.4803 | 540 | 2 | 1223.7612 | 305.9403 | 875.5708
6 | 180 | 预制桩承台基础 | 110000 | 10.25 | 3 | 3 | 1.1 | 1.4 | 1 | 0.6 | 32 | 20 | 640 | 330.0636 | 603.6505 | 50.4803 | 540 | 2 | 1223.7612 | 305.9403 | 875.5708
6 | 180 | 预制桩承台基础 | 120000 | 10.5 | 3 | 3 | 1.2 | 1.4 | 1 | 0.6 | 34 | 20 | 680 | 346.3606 | 664.9181 | 52.9484 | 552 | 2 | 1312.3061 | 328.0765 | 922.5161
6 | 180 | 灌注桩承台基础 | 50000 | 9 | 3 | 3 | 1 | 1.2 | 0.8 | 1 | 18 | 20 | 360 | 254.469 | 424.115 | 39.0233 | 480 | 2 | 839.8947 | 209.9737 | 586.7301
6 | 180 | 灌注桩承台基础 | 60000 | 9.5 | 3 | 3 | 1 | 1.2 | 0.8 | 1 | 20 | 20 | 400 | 283.5287 | 466.6836 | 43.4294 | 480 | 2 | 923.4171 | 230.8543 | 644.1584
6 | 180 | 灌注桩承台基础 | 70000 | 9.5 | 3 | 3 | 1 | 1.2 | 0.8 | 1 | 22 | 20 | 440 | 283.5287 | 466.6836 | 43.4294 | 480 | 2 | 923.4171 | 230.8543 | 644.1584
6 | 180 | 灌注桩承台基础 | 80000 | 10 | 3 | 3 | 1 | 1.4 | 1 | 1 | 24 | 20 | 480 | 314.1593 | 546.2182 | 48.0711 | 528 | 2 | 1139.2659 | 284.8165 | 829.7931
6 | 180 | 灌注桩承台基础 | 90000 | 10 | 3 | 3 | 1 | 1.4 | 1 | 1 | 26 | 20 | 520 | 314.1593 | 546.2182 | 48.0711 | 528 | 2 | 1139.2659 | 284.8165 | 829.7931
6 | 180 | 灌注桩承台基础 | 100000 | 10.25 | 3 | 3 | 1.1 | 1.4 | 1 | 1 | 28 | 20 | 560 | 330.0636 | 603.6505 | 50.4803 | 540 | 2 | 1223.7612 | 305.9403 | 875.5708
6 | 180 | 灌注桩承台基础 | 110000 | 10.25 | 3 | 3 | 1.1 | 1.4 | 1 | 1 | 30 | 20 | 600 | 330.0636 | 603.6505 | 50.4803 | 540 | 2 | 1223.7612 | 305.9403 | 875.5708
6 | 180 | 灌注桩承台基础 | 120000 | 10.5 | 3 | 3 | 1.2 | 1.4 | 1 | 1 | 32 | 20 | 640 | 346.3606 | 664.9181 | 52.9484 | 552 | 2 | 1312.3061 | 328.0765 | 922.5161
7 | 180 | 扩展基础 | 50000 | 9.5 | 3 | 3 | 1 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 283.5287 | 466.6836 | 43.4294 | 480 | 2 | 923.4171 | 230.8543 | 644.1584
7 | 180 | 扩展基础 | 60000 | 10 | 3 | 3 | 1 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 314.1593 | 540.5634 | 48.0711 | 504 | 2 | 1075.0819 | 268.7705 | 755.2179
7 | 180 | 扩展基础 | 70000 | 10.25 | 3 | 3 | 1 | 1.6 | 1 | 0 | 0 | 0 | 0 | 330.0636 | 600.9736 | 50.4803 | 552 | 2 | 1257.2889 | 314.3222 | 920.1573
7 | 180 | 扩展基础 | 80000 | 10.25 | 3 | 3 | 1 | 1.7 | 1 | 0 | 0 | 0 | 0 | 330.0636 | 616.1383 | 50.4803 | 564 | 2 | 1290.8166 | 322.7042 | 946.9022
7 | 180 | 扩展基础 | 90000 | 10.75 | 3 | 3 | 1 | 1.7 | 1 | 0 | 0 | 0 | 0 | 363.0503 | 670.4879 | 55.4754 | 564 | 2 | 1404.9947 | 351.2487 | 1030.2801
7 | 180 | 扩展基础 | 100000 | 11 | 3 | 3 | 1 | 1.8 | 1 | 0 | 0 | 0 | 0 | 380.1327 | 715.6548 | 58.0613 | 576 | 2 | 1501.9213 | 375.4803 | 1103.6855
7 | 180 | 扩展基础 | 110000 | 11.5 | 3 | 3 | 1.1 | 1.8 | 1 | 0 | 0 | 0 | 0 | 415.4756 | 816.5785 | 63.4099 | 588 | 2 | 1667.6881 | 416.922 | 1204.6217
7 | 180 | 扩展基础 | 120000 | 12 | 3 | 3 | 1.2 | 1.8 | 1 | 0 | 0 | 0 | 0 | 452.3893 | 927.3982 | 68.9941 | 600 | 2 | 1844.9782 | 461.2445 | 1309.8305
7 | 180 | 预制桩承台基础 | 50000 | 9 | 3 | 3 | 1 | 1.2 | 0.8 | 0.6 | 20 | 20 | 400 | 254.469 | 424.115 | 39.0233 | 480 | 2 | 839.8947 | 209.9737 | 586.7301
7 | 180 | 预制桩承台基础 | 60000 | 9.5 | 3 | 3 | 1 | 1.2 | 0.8 | 0.6 | 22 | 20 | 440 | 283.5287 | 466.6836 | 43.4294 | 480 | 2 | 923.4171 | 230.8543 | 644.1584
7 | 180 | 预制桩承台基础 | 70000 | 9.5 | 3 | 3 | 1 | 1.2 | 0.8 | 0.6 | 24 | 20 | 480 | 283.5287 | 466.6836 | 43.4294 | 480 | 2 | 923.4171 | 230.8543 | 644.1584
7 | 180 | 预制桩承台基础 | 80000 | 10 | 3 | 3 | 1 | 1.4 | 1 | 0.6 | 26 | 20 | 520 | 314.1593 | 546.2182 | 48.0711 | 528 | 2 | 1139.2659 | 284.8165 | 829.7931
7 | 180 | 预制桩承台基础 | 90000 | 10 | 3 | 3 | 1 | 1.4 | 1 | 0.6 | 28 | 20 | 560 | 314.1593 | 546.2182 | 48.0711 | 528 | 2 | 1139.2659 | 284.8165 | 829.7931
7 | 180 | 预制桩承台基础 | 100000 | 10.25 | 3 | 3 | 1.1 | 1.4 | 1 | 0.6 | 30 | 20 | 600 | 330.0636 | 603.6505 | 50.4803 | 540 | 2 | 1223.7612 | 305.9403 | 875.5708
7 | 180 | 预制桩承台基础 | 110000 | 10.25 | 3 | 3 | 1.1 | 1.4 | 1 | 0.6 | 32 | 20 | 640 | 330.0636 | 603.6505 | 50.4803 | 540 | 2 | 1223.7612 | 305.9403 | 875.5708
7 | 180 | 预制桩承台基础 | 120000 | 10.5 | 3 | 3 | 1.2 | 1.4 | 1 | 0.6 | 34 | 20 | 680 | 346.3606 | 664.9181 | 52.9484 | 552 | 2 | 1312.3061 | 328.0765 | 922.5161
7 | 180 | 灌注桩承台基础 | 50000 | 9 | 3 | 3 | 1 | 1.2 | 0.8 | 1 | 18 | 20 | 360 | 254.469 | 424.115 | 39.0233 | 480 | 2 | 839.8947 | 209.9737 | 586.7301
7 | 180 | 灌注桩承台基础 | 60000 | 9.5 | 3 | 3 | 1 | 1.2 | 0.8 | 1 | 20 | 20 | 400 | 283.5287 | 466.6836 | 43.4294 | 480 | 2 | 923.4171 | 230.8543 | 644.1584
7 | 180 | 灌注桩承台基础 | 70000 | 9.5 | 3 | 3 | 1 | 1.2 | 0.8 | 1 | 22 | 20 | 440 | 283.5287 | 466.6836 | 43.4294 | 480 | 2 | 923.4171 | 230.8543 | 644.1584
7 | 180 | 灌注桩承台基础 | 80000 | 10 | 3 | 3 | 1 | 1.4 | 1 | 1 | 24 | 20 | 480 | 314.1593 | 546.2182 | 48.0711 | 528 | 2 | 1139.2659 | 284.8165 | 829.7931
7 | 180 | 灌注桩承台基础 | 90000 | 10 | 3 | 3 | 1 | 1.4 | 1 | 1 | 26 | 20 | 520 | 314.1593 | 546.2182 | 48.0711 | 528 | 2 | 1139.2659 | 284.8165 | 829.7931
7 | 180 | 灌注桩承台基础 | 100000 | 10.25 | 3 | 3 | 1.1 | 1.4 | 1 | 1 | 28 | 20 | 560 | 330.0636 | 603.6505 | 50.4803 | 540 | 2 | 1223.7612 | 305.9403 | 875.5708
7 | 180 | 灌注桩承台基础 | 110000 | 10.25 | 3 | 3 | 1.1 | 1.4 | 1 | 1 | 30 | 20 | 600 | 330.0636 | 603.6505 | 50.4803 | 540 | 2 | 1223.7612 | 305.9403 | 875.5708
7 | 180 | 灌注桩承台基础 | 120000 | 10.5 | 3 | 3 | 1.2 | 1.4 | 1 | 1 | 32 | 20 | 640 | 346.3606 | 664.9181 | 52.9484 | 552 | 2 | 1312.3061 | 328.0765 | 922.5161
8 | 180 | 扩展基础 | 50000 | 9.5 | 3 | 3 | 1 | 1.2 | 0.8 | 0 | 0 | 0 | 0 | 283.5287 | 466.6836 | 43.4294 | 480 | 2 | 923.4171 | 230.8543 | 644.1584
8 | 180 | 扩展基础 | 60000 | 10 | 3 | 3 | 1 | 1.4 | 0.8 | 0 | 0 | 0 | 0 | 314.1593 | 540.5634 | 48.0711 | 504 | 2 | 1075.0819 | 268.7705 | 755.2179
8 | 180 | 扩展基础 | 70000 | 10.25 | 3 | 3 | 1 | 1.6 | 1 | 0 | 0 | 0 | 0 | 330.0636 | 600.9736 | 50.4803 | 552 | 2 | 1257.2889 | 314.3222 | 920.1573
8 | 180 | 扩展基础 | 80000 | 10.25 | 3 | 3 | 1 | 1.7 | 1 | 0 | 0 | 0 | 0 | 330.0636 | 616.1383 | 50.4803 | 564 | 2 | 1290.8166 | 322.7042 | 946.9022
8 | 180 | 扩展基础 | 90000 | 10.75 | 3 | 3 | 1 | 1.7 | 1 | 0 | 0 | 0 | 0 | 363.0503 | 670.4879 | 55.4754 | 564 | 2 | 1404.9947 | 351.2487 | 1030.2801
8 | 180 | 扩展基础 | 100000 | 11 | 3 | 3 | 1 | 1.8 | 1 | 0 | 0 | 0 | 0 | 380.1327 | 715.6548 | 58.0613 | 576 | 2 | 1501.9213 | 375.4803 | 1103.6855
8 | 180 | 扩展基础 | 110000 | 11.5 | 3 | 3 | 1.1 | 1.8 | 1 | 0 | 0 | 0 | 0 | 415.4756 | 816.5785 | 63.4099 | 588 | 2 | 1667.6881 | 416.922 | 1204.6217
8 | 180 | 扩展基础 | 120000 | 12 | 3 | 3 | 1.2 | 1.8 | 1 | 0 | 0 | 0 | 0 | 452.3893 | 927.3982 | 68.9941 | 600 | 2 | 1844.9782 | 461.2445 | 1309.8305
8 | 180 | 预制桩承台基础 | 50000 | 9 | 3 | 3 | 1 | 1.2 | 0.8 | 0.6 | 20 | 20 | 400 | 254.469 | 424.115 | 39.0233 | 480 | 2 | 839.8947 | 209.9737 | 586.7301
8 | 180 | 预制桩承台基础 | 60000 | 9.5 | 3 | 3 | 1 | 1.2 | 0.8 | 0.6 | 22 | 20 | 440 | 283.5287 | 466.6836 | 43.4294 | 480 | 2 | 923.4171 | 230.8543 | 644.1584
8 | 180 | 预制桩承台基础 | 70000 | 9.5 | 3 | 3 | 1 | 1.2 | 0.8 | 0.6 | 24 | 20 | 480 | 283.5287 | 466.6836 | 43.4294 | 480 | 2 | 923.4171 | 230.8543 | 644.1584
8 | 180 | 预制桩承台基础 | 80000 | 10 | 3 | 3 | 1 | 1.4 | 1 | 0.6 | 26 | 20 | 520 | 314.1593 | 546.2182 | 48.0711 | 528 | 2 | 1139.2659 | 284.8165 | 829.7931
8 | 180 | 预制桩承台基础 | 90000 | 10 | 3 | 3 | 1 | 1.4 | 1 | 0.6 | 28 | 20 | 560 | 314.1593 | 546.2182 | 48.0711 | 528 | 2 | 1139.2659 | 284.8165 | 829.7931
8 | 180 | 预制桩承台基础 | 100000 | 10.25 | 3 | 3 | 1.1 | 1.4 | 1 | 0.6 | 30 | 20 | 600 | 330.0636 | 603.6505 | 50.4803 | 540 | 2 | 1223.7612 | 305.9403 | 875.5708
8 | 180 | 预制桩承台基础 | 110000 | 10.25 | 3 | 3 | 1.1 | 1.4 | 1 | 0.6 | 32 | 20 | 640 | 330.0636 | 603.6505 | 50.4803 | 540 | 2 | 1223.7612 | 305.9403 | 875.5708
8 | 180 | 预制桩承台基础 | 120000 | 10.5 | 3 | 3 | 1.2 | 1.4 | 1 | 0.6 | 34 | 20 | 680 | 346.3606 | 664.9181 | 52.9484 | 552 | 2 | 1312.3061 | 328.0765 | 922.5161
8 | 180 | 灌注桩承台基础 | 50000 | 9 | 3 | 3 | 1 | 1.2 | 0.8 | 1 | 18 | 20 | 360 | 254.469 | 424.115 | 39.0233 | 480 | 2 | 839.8947 | 209.9737 | 586.7301
8 | 180 | 灌注桩承台基础 | 60000 | 9.5 | 3 | 3 | 1 | 1.2 | 0.8 | 1 | 20 | 20 | 400 | 283.5287 | 466.6836 | 43.4294 | 480 | 2 | 923.4171 | 230.8543 | 644.1584
8 | 180 | 灌注桩承台基础 | 70000 | 9.5 | 3 | 3 | 1 | 1.2 | 0.8 | 1 | 22 | 20 | 440 | 283.5287 | 466.6836 | 43.4294 | 480 | 2 | 923.4171 | 230.8543 | 644.1584
8 | 180 | 灌注桩承台基础 | 80000 | 10 | 3 | 3 | 1 | 1.4 | 1 | 1 | 24 | 20 | 480 | 314.1593 | 546.2182 | 48.0711 | 528 | 2 | 1139.2659 | 284.8165 | 829.7931
8 | 180 | 灌注桩承台基础 | 90000 | 10 | 3 | 3 | 1 | 1.4 | 1 | 1 | 26 | 20 | 520 | 314.1593 | 546.2182 | 48.0711 | 528 | 2 | 1139.2659 | 284.8165 | 829.7931
8 | 180 | 灌注桩承台基础 | 100000 | 10.25 | 3 | 3 | 1.1 | 1.4 | 1 | 1 | 28 | 20 | 560 | 330.0636 | 603.6505 | 50.4803 | 540 | 2 | 1223.7612 | 305.9403 | 875.5708
8 | 180 | 灌注桩承台基础 | 110000 | 10.25 | 3 | 3 | 1.1 | 1.4 | 1 | 1 | 30 | 20 | 600 | 330.0636 | 603.6505 | 50.4803 | 540 | 2 | 1223.7612 | 305.9403 | 875.5708
8 | 180 | 灌注桩承台基础 | 120000 | 10.5 | 3 | 3 | 1.2 | 1.4 | 1 | 1 | 32 | 20 | 640 | 346.3606 | 664.9181 | 52.9484 | 552 | 2 | 1312.3061 | 328.0765 | 922.5161

## 箱变基础数据
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
风机容量 | 箱变容量 | 长 | 宽 | 高 | 壁厚 | 压顶高 | C35混凝土压顶 | C15垫层 | MU10砖 | 钢筋 | 面积 | 土方开挖 | 石方开挖 | 土石回填
Turbinecapacity | convertingstation | long | width | high | Wallthickness | Highpressure | C35concretetop | C15cushion | MU10brick | Reinforcement | area | Earthexcavation | Stoneexcavation | Earthworkbackfill
2 | 2200 | 4.9 | 3.65 | 1.8 | 0.25 | 0.5 | 2.0125 | 4.1153 | 5.2325 | 0.20125 | 17.885 | 35.1168 | 8.7792 | 15.28
2.2 | 2500 | 5 | 4 | 1.8 | 0.25 | 0.5 | 2.125 | 4.5 | 5.525 | 0.2125 | 20 | 38.4 | 9.6 | 16
2.5 | 2750 | 6 | 4 | 1.8 | 0.25 | 0.5 | 2.375 | 5.25 | 6.175 | 0.2375 | 24 | 44.8 | 11.2 | 17.6
3 | 3300 | 6 | 4.5 | 1.8 | 0.25 | 0.5 | 2.5 | 5.775 | 6.5 | 0.25 | 27 | 49.28 | 12.32 | 18.4
3.2 | 3520 | 6 | 5.5 | 1.8 | 0.25 | 0.5 | 2.75 | 6.825 | 7.15 | 0.275 | 33 | 58.24 | 14.56 | 20
3.3 | 3520 | 6 | 5.5 | 1.8 | 0.25 | 0.5 | 2.75 | 6.825 | 7.15 | 0.275 | 33 | 58.24 | 14.56 | 20
3.4 | 3520 | 6 | 5.5 | 1.8 | 0.25 | 0.5 | 2.75 | 6.825 | 7.15 | 0.275 | 33 | 58.24 | 14.56 | 20
3.6 | 4000 | 6 | 6 | 1.8 | 0.25 | 0.5 | 2.875 | 7.35 | 7.475 | 0.2875 | 36 | 62.72 | 15.68 | 20.8

## 升压站基础数据
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27
状态 | 等级 | 容量 | 长 | 宽 | 围墙内面积 | 围墙长度 | 浆砌石护脚 | 浆砌石排水沟 | 道路面积 | 绿化面积 | 综合楼 | 设备楼 | 附属楼 | 主变基础C30混凝土 | C15混凝土垫层 | 主变压器基础钢筋 | 事故油池C30混凝土 | 事故油池C15垫层 | 事故油池钢筋 | 设备及架构基础C25混凝土 | 室外架构（型钢） | 预制混凝土杆 | 避雷针 | 土方开挖 | 石方开挖 | 土方回填 | 放坡面积
status | grade | capacity | long | width | Innerwallarea | Walllength | Stonemasonryfoot | Stonemasonrydrainageditch | Roadarea | Greenarea | Comprehensivebuilding | Equipmentbuilding | Affiliatedbuilding | C30concrete | C15concretecushion | Maintransformerfoundation | AccidentoilpoolC30concrete | AccidentoilpoolC15cushion | Accidentoilpoolreinforcement | FoundationC25Concrete | Outdoorstructure | Precastconcretepole | lightningrod | Earthexcavation | Stoneexcavation | Earthworkbackfill | Slopearea
新建 | 110 | 50 | 88.8 | 86.7 | 7698.96 | 351 | 351 | 175.5 | 1666.45 | 840.2 | 1316.8 | 510 | 370.44 | 60 | 12 | 6 | 30 | 5 | 1 | 100 | 3 | 80 | 1 | #REF! | #REF! | #REF! | #REF!
新建 | 110 | 100 | 103.3 | 98.61 | 10186.413 | 403.82 | 403.82 | 201.91 | 1993.67 | 1200 | 1316.8 | 510 | 370.44 | 120 | 20 | 10 | 60 | 10 | 2 | 200 | 5 | 150 | 2 | #REF! | #REF! | #REF! | #REF!
新建 | 110 | 150
新建 | 110 | 200
新建 | 220 | 50
新建 | 220 | 100
新建 | 220 | 150
新建 | 220 | 200
利用原有 | 110 | 50 | [11 empty] | 60 | 12 | 6
利用原有 | 110 | 100 | [11 empty] | 60 | 12 | 6
利用原有 | 110 | 150 | [11 empty] | 60 | 12 | 6
利用原有 | 110 | 200 | [11 empty] | 60 | 12 | 6
利用原有 | 220 | 50 | [11 empty] | 60 | 12 | 6
利用原有 | 220 | 100 | [11 empty] | 60 | 12 | 6
利用原有 | 220 | 150 | [11 empty] | 60 | 12 | 6
利用原有 | 220 | 200 | [11 empty] | 60 | 12 | 6

## 道路基础数据1
场外改扩建道路 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
山地类型 | 级配碎石路面(20cm厚) | D1000mm圆管涵 | 浆砌石排水沟 | M7.5浆砌片石挡墙 | 草皮护坡 | 土方开挖 | 石方开挖 | 土石方回填
terrain_type | Gradedgravelpavement | roundtubeculvert | Stonemasonrydrainageditch | mortarstoneretainingwall | Turfslopeprotection | Earthexcavation | Stoneexcavation | Earthworkbackfill | Slopearea
平原 | 2500 | 0 | 475 | 0 | 1000 | 800 | 200 | 1000
丘陵 | 2500 | 0 | 475 | 0 | 1000 | 800 | 200 | 1000
缓坡低山 | 2500 | 0 | 475 | 100 | 1500 | 2000 | 500 | 1250
陡坡低山 | 2500 | 0 | 475 | 150 | 2000 | 4000 | 1000 | 1250
缓坡中山 | 2500 | 0 | 475 | 100 | 1000 | 3000 | 750 | 1250
陡坡中山 | 2500 | 0 | 475 | 200 | 1000 | 5000 | 1250 | 1250
缓坡高山 | 2500 | 0 | 475 | 100 | 1000 | 4000 | 1000 | 1250
陡坡高山 | 2500 | 0 | 475 | 250 | 1000 | 6000 | 1500 | 1250

## 道路基础数据2
进站道路 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
山地类型 | 级配碎石基层(20cm厚) | C30混凝土路面(20cm厚) | D1000mm圆管涵 | 浆砌石排水沟 | M7.5浆砌片石挡墙 | 草皮护坡 | 标志标牌 | 波形护栏 | 土方开挖 | 石方开挖 | 土石方回填
terrain_type
平原 | 6500 | 6000 | 0 | 475 | 0 | 1000 | 2 | 0 | 1560 | 390 | 3250
丘陵 | 6500 | 6000 | 0 | 475 | 100 | 2000 | 2 | 0 | 4800 | 1200 | 3000
缓坡低山 | 6500 | 6000 | 20 | 475 | 200 | 5000 | 2 | 160 | 6400 | 1600 | 4000
陡坡低山 | 6500 | 6000 | 20 | 475 | 300 | 6000 | 2 | 200 | 12000 | 3000 | 4500
缓坡中山 | 6500 | 6000 | 20 | 475 | 250 | 5000 | 2 | 180 | 8000 | 2000 | 5000
陡坡中山 | 6500 | 6000 | 20 | 475 | 350 | 7000 | 2 | 250 | 14400 | 3600 | 5400
缓坡高山 | 6500 | 6000 | 20 | 475 | 300 | 6000 | 2 | 200 | 9600 | 2400 | 6000
陡坡高山 | 6500 | 6000 | 20 | 475 | 400 | 8000 | 2 | 300 | 16000 | 4000 | 6000

## 道路基础数据3
施工检修道路工程 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
山地类型 | 山皮石路面(20cm厚) | C30混凝土路面(20cm厚) | D1000mm圆管涵 | 浆砌石排水沟 | M7.5浆砌片石挡墙 | 草皮护坡 | 标志标牌 | 波形护栏 | 用地 | 土方开挖 | 石方开挖 | 土石方回填 | 桥梁
terrain_type
平原 | 5500 | 0 | 20 | 475 | 0 | 1000 | 2 | 0 | 8000 | 1560 | 390 | 3250
丘陵 | 6000 | 0 | 20 | 475 | 100 | 2000 | 2 | 0 | 10000 | 4800 | 1200 | 3000
缓坡低山 | 6000 | 0 | 20 | 475 | 200 | 5000 | 4 | 160 | 10000 | 6400 | 1600 | 4000
陡坡低山 | 6000 | 0 | 20 | 475 | 300 | 6000 | 4 | 200 | 12000 | 12000 | 3000 | 4500
缓坡中山 | 6000 | 0 | 20 | 475 | 250 | 5000 | 4 | 180 | 11000 | 8000 | 2000 | 5000
陡坡中山 | 6000 | 0 | 20 | 475 | 350 | 7000 | 4 | 250 | 13000 | 14400 | 3600 | 5400
缓坡高山 | 6000 | 0 | 20 | 475 | 300 | 6000 | 4 | 200 | 12000 | 9600 | 2400 | 6000
陡坡高山 | 6000 | 0 | 20 | 475 | 400 | 8000 | 4 | 300 | 14000 | 16000 | 4000 | 6000

## 道路基础数据4
山地类型 | 吊装平台工程 | 一般场地平整 | 土方开挖 | 石方开挖 | 土石方回填 | 浆砌石排水沟 | M7.5浆砌片石护坡 | 草皮护坡
terrain_type
平原 |  | 1800 | 288 | 72 | 360 | 0 | 0 | 1800
丘陵 |  | 1800 | 2880 | 720 | 1800 | 19 | 0 | 1800
缓坡低山 |  | 1800 | 2880 | 720 | 1800 | 19 | 0 | 1800
陡坡低山 |  | 1800 | 4320 | 1080 | 900 | 19 | 50 | 1800
缓坡中山 |  | 1800 | 3600 | 900 | 1800 | 19 | 20 | 1800
陡坡中山 |  | 1800 | 5040 | 1260 | 900 | 19 | 50 | 1800
缓坡高山 |  | 1800 | 3600 | 900 | 1800 | 19 | 20 | 1800
陡坡高山 |  | 1800 | 5760 | 1440 | 900 | 19 | 50 | 1800